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Members Present:

 Sandy Battreall (Beaver Lake Board, BLA, Representative), Troy Weatherby, (Operations Manager), Jim Wieringa  (Utility Committee Chairman), Pat Diederich,  Dale Long, and Mike Pfeiffer were in attendance.  Ramon Fusaro, John Frost, and Phil Lamoureux, were absent.  The January minutes and today’s agenda were reviewed and approved.  
Old Business:  


- Monthly report of Utility Functions: 
There were no water or sewer leaks in January.  The only water loss was an estimated loss of 11,200 gallons for flushing the chlorine analyzer at the Alternate Drinking Water Supply Building 
Sewer water influent from Murray in January was again very high.  It was almost 2 million gallons and most likely due to ground water and runoff going into sewer system. 
 Troy said there is one possible location at Beaver Lake where ground water is leaking into the sewer system.  This summer it will be checked out.
Work completed in January or scheduled for February:
1) Lift Station (LS) 10 plans were reviewed by Troy and John.  Several changes need to be made.  Changes should be incorporated and plans sent to the state for approval this week.  Hopefully state review will be completed and permit issued for construction by end of March 2016.
2) Troy Submitted the 2015 Tier II chemical storage inventory plan to the NDEQ.

3) Troy will begin drawings for the LS 10 valve vault. 
4) BLA staff will degrease all lift stations this month.  Residents dump grease down their drains and it congeals in the lift stations.  
5) Three Beaver Lake employees have finished three courses in the emergency management.  Two employees are working on completing the courses.  
6) Repairs were made to an underground electrical line that provided power to the heaters in the clear well valve vault.
-New Business: None
-Next meeting: The next meeting is scheduled for 7 March 2016 at 6 P.M. The meeting        adjourned at 6:50.
