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Members Present:

 Dale Long (Beaver Lake Board, BLA, Representative), Troy Weatherby, (Operations Manager), Jim Wieringa  (Utility Committee Chairman), Pat Diederich,  Ramon Fusaro, John Frost, Phil Lamoureux, and Mike Pfeiffer were in attendance.  Also attending were guests Bill Haney, Mike Bonnstetter, and Sandy Battreall.  The April minutes and today’s agenda were reviewed and approved.  
Old Business:  


- Monthly report of Utility Functions: 
There were no water or sewer leaks in May.  The only loss was an estimated loss of 5,900 gallons for flushing the chlorine analyzer at the Alternate Drinking Water Supply Building.  
The raw water flow meter for the water plant failed.  Since it was installed in 1996, parts are not available to repair it.  A new meter has been ordered and will take approximately one day to install.  Until new meter is installed water is being pumped from lake based on past experience.

The sewer plant operated at 77% of capacity versus normal of 49% for the month of May.  The additional sewer water came from Murray and is due to ground and rain water seeping into the sewer lines or manholes.  As more homes are built at Beaver Lake and Lake Ridge this could cause the sewer plant to be overloaded.  Troy says Murray has been told they have problems but to date they are not addressing them. 
Lift Station (LS) 8 was flooded by water crossing the road during a heavy rain.  Luckily the control panel stayed above the water and LS 8 pumped the water down and no damage to the lift station occurred.  
Work completed in May or scheduled for June
1) Inflow from Lake Ridge was inspected and found to be in fairly good condition..  
2) Work required by State Inspector at LS 11 has been completed.  Waiting for the lift station to be reinspected.  

3) The vault for LS 10 has been ordered.  Expect installation to start end of July.  

4) At LS 13 all components except meter socket are on hand.  Will start upgrade shortly,  

5) Will start installation of meter pits shortly.  Expect work to be completed by September.
New Business:  
 New Committee Member:  

With Dale Long being elected to the Beaver Lake Board there is one vacant position on the Utility committee.  Bill Haney, Mike Bonnstetter and Sandy Battreall are interested and spoke about how their experience would be beneficial to the committee.  After hearing their qualifications Mike Pfeiffer decided to resign so two positions were available.  The committee voted to recommend to the board that Bill Haney and Mike Bonnstsetter be recommended for approval.  

Next meeting: The date for the July 2016 wasn’t set due to the 4th of July.   The meeting adjourned at 6:50.
