Beaver Lake Utility Committee Minutes
November 4, 2019

[bookmark: _GoBack]Members present; Troy Weatherby (Managing Director), Jim Wieringa	(Chair), John Frost, Bill Haney, Phil Lamoureux, Richard Randal, Jim Claypool, Tom Barry and Bill Barret (Bd Rep)									
Members absent; none

1. No agenda additions, approved unanimously.

2. Review minutes from Oct 7, 2019 meeting.

3. Old business; Monthly report of Utility functions & Projects report and review 

4. New Business
4.1 Discuss the influent sewage from the Village of Murray 
· The yearly contract is 18 million gallons per year
· As of October the amount is 1.3 million gallons over the contract 
· This equates to $3,790.00

4.2 Johnson Control was hired to scope the drainage pipe from Lift station 7 		to 8
· 1850 feet was done at a price of $2,500
· Pictures were obtained showing leakage

4.3  The water treatment plant had software problems over the weekend 
· The plant was run manually
· A computer specialist was obtained and found a corroded wire in the electrical system
                                                              
4.4. The north and south water towers valve replacements and sandblasting 	moved to spring

4.5 Lift station 11
· The lower unit of the pump failed and is the process of being repaired

Meeting adjourned at 7:00 pm.

Next meeting: December 2, 2019 at 6:00 pm.

